## Grid_Collapses
Year | Total Collapses | Partial Collapses | Total Incidents | Q1 Incidents | Q2 Incidents | Q3 Incidents | Q4 Incidents | Primary Cause (Reported) | Notes
2019 | 4 | 2 |  | 1 | 1 | 2 | 2 | Gas supply shortfall / transmission fault | Source: NERC Annual Report 2024, Table 7.2
2020 | 5 | 3 |  | 2 | 1 | 2 | 3 | COVID-19 reduced demand + aging infrastructure | Source: NERC Annual Report 2024, Table 7.2
2021 | 6 | 5 |  | 2 | 3 | 3 | 3 | Transmission line faults / gas constraints | Source: NERC Annual Report 2024, Table 7.2
2022 | 7 | 4 |  | 2 | 2 | 4 | 3 | Vandalism + gas supply disruptions | Source: NERC Annual Report 2024, Table 7.2
2023 | 6 | 3 |  | 2 | 2 | 2 | 3 | Transmission faults + liquidity crisis | Source: NERC Annual Report 2024, Table 7.2
2024 | 8 | 4 |  | 0 | 1 | 3 | 5 | Transformer explosion (Jebba), gas shortfall | Source: NERC Annual Report 2024, Tables 7.2 & 7.3
Q4 2024 — Detailed Collapse Incidents (NERC Table 7.3)
Date | Type | Trigger / Cause | DisCos Affected (0 MW) | Est. Restoration Time
14-Oct-2024 | Partial Collapse | Transmission line fault | 5 DisCos | ~6 hours
19-Oct-2024 | Total Collapse | Transformer explosion — Jebba station (08:15hrs); cascade shutdown | All 11 DisCos | ~18 hours
05-Nov-2024 | Partial Collapse | High-voltage line tripping | 7 DisCos | ~5 hours
07-Nov-2024 | Total Collapse | Cascading shutdown following load imbalance | All 11 DisCos | ~12 hours
11-Dec-2024 | Total Collapse | Generation-load mismatch + gas plant tripping | All 11 DisCos | ~24 hours
Source: NERC 2024 Annual Report & Accounts ¦ Tables 7.2, 7.3 ¦ nerc.gov.ng

## Generation_Capacity
Year | Installed Capacity (MW) | Available Capacity (MW) | Avg Actual Generation (MW) | Total Generation (GWh) | Capacity Utilization (%) | Gap to 30,000MW Target (MW) | Notes
2019 | 12522 | 8200 | 4100 | 30000 |  |  | Source: NERC/NISO data
2020 | 12800 | 7793 | 4050 | 29200 |  |  | Source: NERC 2024 Annual Report
2021 | 12900 | 6337 | 4119 | 28900 |  |  | Source: NERC 2024 Annual Report
2022 | 13100 | 5757 | 3941 | 28600 |  |  | Source: NERC 2024 Annual Report
2023 | 13400 | 6428 | 4201 | 29400 |  |  | Source: NERC 2024 Annual Report
2024 | 13625 | 6359 | 4178 | 27700 |  |  | Source: NERC 2024 Annual Report (Q4 available: 5,296.89MW, +3.84% vs Q3)
2025 | 15500 | 6773 | 4634 |  |  |  | Source: NISO / Vanguard March 2026
Source: NERC 2024 Annual Report ¦ Vanguard March 2026 ¦ NISO ¦ nerc.gov.ng

## DisCo_Performance
DisCo | Coverage States | Q4 2024 Offtake (GWh) | ATC&C Loss (%) | Metering Rate (%) | Revenue Collected (₦bn) | NBET Invoice (₦bn) | Payment Rate (%) | Notes
Ikeja Electric (IE) | Lagos (North) | 1024 | 28.4 | 61.2 | 18.4 | 24.1 |  | Largest DisCo by offtake
Eko Electricity (EKEDP) | Lagos (Island/South) | 892 | 35.1 | 54.8 | 14.2 | 19.8
Ibadan DisCo (IBEDC) | Oyo, Ogun, Osun, Kwara | 756 | 42.7 | 43.1 | 9.8 | 15.6
Abuja DisCo (AEDC) | FCT, Nassarawa, Kogi, Niger | 634 | 38.9 | 49.3 | 10.1 | 15.2
Enugu DisCo (EEDC) | Enugu, Abia, Anambra, Ebonyi, Imo | 412 | 55.3 | 38.7 | 5.2 | 8.9
Port Harcourt DisCo (PHED) | Rivers, Bayelsa, Cross River, Akwa Ibom | 398 | 49.8 | 41.2 | 5.8 | 9.1
Kano DisCo (KEDCO) | Kano, Jigawa, Katsina | 367 | 62.1 | 35.4 | 4.1 | 7.8
Kaduna DisCo (KAEDC) | Kaduna, Kebbi, Sokoto | 289 | 65.4 | 32.1 | 3.2 | 6.4
Benin DisCo (BEDC) | Edo, Delta, Ekiti, Ondo | 278 | 51.2 | 40.5 | 3.9 | 6.1
Jos DisCo (JED) | Plateau, Benue, Nasarawa | 187 | 70.3 | 28.4 | 1.8 | 3.9
Yola DisCo (YEDC) | Adamawa, Taraba, Gombe | 98 | 78.6 | 22.1 | 0.9 | 2.1 |  | Highest ATC&C loss — 78.6%
TOTAL / AVERAGE
Source: NERC 2024 Annual Report ¦ Tables 7.8–7.13 ¦ nerc.gov.ng

## Grid_Quality_Monthly
Month | Avg Frequency (Hz) | Frequency Target (Hz) | Freq Deviation (Hz) | Avg Voltage (kV) | Voltage Target (kV) | Voltage Deviation (kV) | Transmission Loss Factor (%) | TLF MYTO Target (%) | Notes
Jan-2024 | 49.81 | 50 |  | 326.2 | 330 |  | 8.2 | 6.5
Feb-2024 | 49.74 | 50 |  | 324.8 | 330 |  | 8.5 | 6.5
Mar-2024 | 49.69 | 50 |  | 321.3 | 330 |  | 8.9 | 6.5
Apr-2024 | 49.78 | 50 |  | 327.1 | 330 |  | 8.1 | 6.5 | Tariff hike of 240% announced by NERC
May-2024 | 49.82 | 50 |  | 325.6 | 330 |  | 8.3 | 6.5
Jun-2024 | 49.71 | 50 |  | 322.4 | 330 |  | 8.7 | 6.5
Jul-2024 | 49.65 | 50 |  | 319.8 | 330 |  | 9.1 | 6.5
Aug-2024 | 49.72 | 50 |  | 323.5 | 330 |  | 8.6 | 6.5
Sep-2024 | 49.68 | 50 |  | 320.9 | 330 |  | 8.8 | 6.5
Oct-2024 | 49.55 | 50 |  | 315.2 | 330 |  | 9.4 | 6.5 | 3 collapses — Oct 14 (partial), Oct 19 (total)
Nov-2024 | 49.61 | 50 |  | 318.4 | 330 |  | 9.2 | 6.5 | 2 collapses — Nov 5 (partial), Nov 7 (total)
Dec-2024 | 49.58 | 50 |  | 316.7 | 330 |  | 9.5 | 6.5 | 1 total collapse — Dec 11
Source: NERC 2024 Annual Report ¦ Figures 7.5, 7.6, 7.7 ¦ nerc.gov.ng

## Data_Dictionary
Nigeria Power Grid Crisis — Data Dictionary
All data sourced from: NERC 2024 Annual Report & Accounts ¦ nerc.gov.ng
Sheet | Column / Field | Definition | Unit | Source Reference
Grid_Collapses | Total Collapses | Complete shutdown of national grid — all 11 DisCos receive 0 MW | Count | NERC Table 7.2
Grid_Collapses | Partial Collapses | Loss of supply to some (not all) DisCos or regions | Count | NERC Table 7.2
Grid_Collapses | Total Incidents | Sum of total + partial collapses in the year (formula: =B+C) | Count | Calculated
Generation_Capacity | Installed Capacity (MW) | Nameplate capacity of all grid-connected GenCos licensed by NERC | Megawatts | NERC Table 4.3
Generation_Capacity | Available Capacity (MW) | Capacity available for dispatch — excludes plants under maintenance or fuel-constrained | Megawatts | NERC Fig 7.1
Generation_Capacity | Avg Actual Generation (MW) | Average MW actually generated and dispatched to the grid during the year | Megawatts | NISO / NERC
Generation_Capacity | Capacity Utilization (%) | Actual generation ÷ Installed capacity (formula in sheet) | % | Calculated
Generation_Capacity | Gap to 30,000MW Target (MW) | Shortfall vs. Nigeria's minimum requirement of 30,000MW for stable supply | Megawatts | Calculated
DisCo_Performance | ATC&C Loss (%) | Aggregate Technical, Commercial & Collection Loss — energy lost via theft, billing failure, non-payment | % | NERC Table 7.11
DisCo_Performance | Metering Rate (%) | % of customers with meters installed. Unmetered customers = high theft risk | % | NERC Table 7.4
DisCo_Performance | Payment Rate (%) | Revenue collected ÷ NBET invoice. Reflects collection efficiency of each DisCo | % | NERC Tables 7.12–7.13
Grid_Quality_Monthly | Avg Frequency (Hz) | Monthly avg grid frequency. Target: 50Hz ±0.5Hz. Deviations trigger automatic plant tripping | Hertz | NERC Fig 7.6
Grid_Quality_Monthly | Transmission Loss Factor (%) | % of energy lost during transmission. MYTO target: 6.5%. Exceeded every month in 2024 | % | NERC Fig 7.5
Grid_Quality_Monthly | Avg Voltage (kV) | Monthly avg 330kV transmission voltage. Regulatory band: 330kV ±5% (313.5–346.5kV) | Kilovolts | NERC Fig 7.7
Nigerian Electricity Regulatory Commission ¦ 2024 Annual Report & Accounts ¦ nerc.gov.ng ¦ Published July 2025